Digital Multi-Channel Gas Detection System for Methane (CH4)

Provide a wall mount, field programmable control panel with back-lit, full colour touch screen LCD display, LED alarm indication, and door mounted 90 dB audible alarm with audible silence achieved through the touch screen. There shall be a scrolling LCD display of gas, concentration, and alarm status and a substantial menu system supporting logic style programming. Controller shall provide Modbus communication as a standard to the outside world or optional BACnet. System controller shall be capable of supporting up to 128 gas channels (digital and/or analog) on a RS485 communication bus or with analog inputs. System shall support multiple analog input and/or output modules if required (four only 4 - 20 mA outputs per module) and multiple relay output modules if additional relays are required (four or eight only 5 A SPDT relays per module). The controller shall have 4 on board relays. System digital network wiring shall be 4-wire digital network (2 low voltage power wires and a shielded twisted pair for the communication bus). System analog wiring shall be 3-conductor, 16-18 gauge, shielded. System power requirement is 90 to 240 VAC, 47 to 63 Hz. The controller shall be tested to CSA, UL, CE, and FCC standards and be IP54 rated. Model FCS-M (Modbus output) or FCS-B (BACnet output).

The controller may have one or two internal daughter boards supporting up to four analog inputs each. Model FCS-M-AI = four analog input channels. FCS-M-2AI = eight analog input channels.

Provide remote mount analog sensor/transmitter model CXT-A-ICH4 with poison proof infrared sensor for methane (CH4) with a detection range of 0 – 100% LEL. The sensor / transmitter shall be housed in a rugged, wall mount, cast aluminum, explosion-proof junction box suitable for hazardous area installation. The transmitter shall have a glass viewing window with LCD digital display indicating gas values and alarm indicators. The remote mount transmitter shall operate on power supplied by the control panel, and shall provide a 4-20 mA analog output signal to the control panel. Install the CH4 sensor on or near the ceiling as methane is lighter than air.

In all cases follow local codes for installation of wiring and conduit into an explosion rated device. Failure to do so may void any damage from water intrusion or other hazard.

Provide remote mount audible, visual (strobe/siren) alarms model RSH-24-W to be mounted at higher elevations and activated upon any high alarm condition to alert workers of gas build up beyond high alarm concentration. The RSH-24 will be powered by installer supplied 24VAC power and controlled by the controller relays.

System operation shall be as follows: Upon detection of 10% LEL methane the system shall illuminate the Low alarm LED, the Low alarm relays and anything controlled by these relays will be activated immediately. Upon detection of 20% LEL methane the system shall illuminate the High alarm LED, the High alarm relays and anything controlled by these relays will be activated and the system audible alarm will be activated. Audible alarm can be silenced from the front touch panel. Any remote alarm devices shall be activated at this alarm level as well.

The contractor shall provide all wiring (network and analog), conduit and interconnection required for a successful installation. System shall be tested and commissioned after installation by a trained, authorized service representative of the manufacturer, with a detailed service report provided after the site visit.

Approved manufacturer: Critical Environment Technologies Canada Inc.