Refrigerant Leak Detection System, Semi-conductor for R134A Refrigerant

Provide a wall mount, control panel with back-lit, LCD digital display, LED alarm indication, and 80 dB audible alarm with silence / acknowledge button integrated into the Lexan label all housed in a rugged, water/dust tight IP54 rated polycarbonate/ABS enclosure with secured, hinged door. The controller shall have a display of gas concentration, and alarm status.  Controller shall be capable of supporting one remote analog sensor/transmitter. Controller shall provide two 4-20 mA analog outputs. Controller shall provide two dry contact relays rated 5 A @ 240VAC SPDT each. Controller wiring to remote sensor/transmitter shall be 3-conductor, 16-18 gauge, and stranded, shielded. System power requirement is 90 to 240 VAC, 47 to 63 Hz or low voltage 16-30VDC or 12-28 VAC. The controller shall be tested to CSA/UL/CE and FCC standards. Model DCC-B-RT.

Provide one remote mount analog transmitter model LPT-A-SR134A for R134A Freon with semi-conductor refrigerant sensor with a detection range of 0 - 2000 ppm. The sensor / transmitter shall be housed in a rugged, wall mount, ABS/polycarbonate junction box. An optional splash cover is available for hose down applications (add suffix “S” to part number). The remote mount transmitter shall operate on power supplied by the control panel, and shall provide an analog output signal to the control panel. Install the R134A sensor in an area where refrigerant vapour from a leak will most likely be concentrated.

In all cases use liquid tight conduit hubs when entering any enclosure with attached splash cover to reduce water intrusion. Install to the wall only by the provided enclosure mounting locations. Failure to do so voids any warranty for damage from water intrusion.

Provide remote mount audible, visual (strobe/siren) alarm model RSH-24VDC to be mounted at higher elevations and activated upon any high alarm condition to alert workers of gas build up beyond high alarm concentration. The RSH-24 will be powered by installer supplied 24VAC/VDC power and controlled by the controller relays.

System operation shall be as follows: Upon detection of 250 ppm R134A, the system shall illuminate the Low alarm LED, the Low alarm relay (typically controlling the exhaust fan) will be activated immediately. The system shall keep the fans running for a minimum of 10 minutes to avoid cycling the fan or until the level of leaked refrigerant is below the alarm threshold. Upon detection of 500 ppm R134A, the system shall illuminate the Mid alarm LED and the Mid alarm relay will be activated, (only if any relay has been assigned as a mid-alarm). The system shall keep the Mid relay active for a minimum of 10 minutes. Upon detection of 1000 ppm R134A, the system shall illuminate the High alarm LED, the High alarm relay and all door mounted audible alarms and strobe lights, inside and outside the door will be activated. The system shall keep the High relay active until the alarm condition has been acknowledged. Audible alarm can be silenced from the integrated silence button on the DCC label. Any remote alarm devices shall be activated at this alarm level as well.

The contractor shall provide all wiring (analog), conduit and interconnection required for a successful installation. Wiring must be 16-18 gauge, stranded, shielded. System shall be tested and commissioned after installation by a trained, authorized service representative of the manufacturer, with a detailed service report provided after the site visit.

Approved manufacturer:

Critical Environment Technologies Canada Inc.