Welding Fume - Gas Detection System for Carbon Monoxide (CO) and Nitrogen Dioxide (NO2)

Supply a dual channel, self-contained gas detection system, Model DCC-E-TCO-NO2B, for the monitoring of Carbon Monoxide and Nitrogen Dioxide, housed in a rugged, wall mount, water/dust tight polycarbonate enclosure with hinged, secured door and splash guard for installation in areas where moisture or dust and dirt are of concern. Option -S

System power shall be Low Voltage (24 VAC or VDC) or Line Voltage (90 – 240 VAC) capable. The system shall have two integral electrochemical sensors, one CO with measurement range of 0 - 200 ppm CO in air and one NO2 with measurement range of 0 - 10 ppm NO2 in air. The system must be accurate enough to measure to government workplace hazardous gas exposure standards. Area of monitoring coverage is up to 5,000 to 7,000 square feet per sensor system.

The self-contained gas detection system shall provide an LED indicating light for power, low alarm, high alarm, and fault condition plus channel indication LEDs, a 2x16 character LCD digital display indicating “CH1” state, “CH2” state, and FAULT”, an integral audible alarm with silence push-button, two SPDT dry contact alarm relays, each rated 5 A at 240 VAC as well as a 4 – 20 mA output for each sensor indicating the level of the target gas sensed within the measurement range. The system shall also provide field adjustable time delays for “delays on make” and “delays on break” for each sensor to allow custom configuration of ventilation control by the system relays, if desired.

The self-contained gas detection system shall be set-up, programmed and calibrated at the factory for operation upon installation and shall provide a circuit test function to allow for confirmation of system operation and exhaust fan control from the panel. Installation height for the self-contained gas detection system is 4’ to 6’ from the floor.

System operation shall be as follows:

System relays are normally energized in non-gas-alarm state so they act in fail-safe operation.

Upon detection of 25 ppm CO in air or 0.7 ppm NO2 in air, the system shall illuminate the Low alarm LED (amber) and the low gas alarm relay shall de-energize activating single-speed exhaust fans or low speed of two-speed exhaust fans plus make up air fans.

Upon detection of 100 ppm CO in air or 1.5 ppm NO2, the system shall illuminate the High alarm LED (red), the system audible alarm will be activated and the high gas alarm relay shall de-energize activating high speed of two-speed exhaust fans or remote alarm devices.

The 4 – 20 mA outputs shall be linear to the concentration of the target gas measured in the ambient atmosphere with the 4 mA indicating 0 ppm and the 20 mA indicating the top end of the measurement range for that sensor (i.e.; 200 ppm for CO and 10 ppm for NO2).

The integral audible alarm can be silenced from the front panel push button. In the event of a fail condition, the system audible alarm shall be activated and the fail LED on the front panel shall illuminate red and the LCD shall show which channel (sensor) is in fail mode.

The contractor shall provide all wiring, conduit and interconnection required for a successful installation.

Approved manufacturer:

Critical Environment Technologies Canada Inc.