Digital Multi-Channel Gas Detection System for Carbon Monoxide (CO) & Nitrogen Dioxide (NO2)

Provide a wall mount, field programmable control panel with back-lit, full colour touch screen LCD, with LED alarm indication, and door mounted 90 dB audible alarm with silence / acknowledge membrane switch. There shall be a summary LCD display of gas, concentration, and alarm status and user accessible menu system.  System controller shall be capable of supporting up to 128 digital transmitters on a RS485 communication bus or up to 60 analog transmitters. System shall support analog output modules if required (four only 4 - 20 mA outputs per module) and relay output modules if additional relays are required (four or eight only 5 A SPDT relays per module). The controller shall have 4 on board relays. System digital network wiring shall be 4-wire digital network (2 low voltage power wires and a shielded twisted pair for the communication bus). System analog wiring shall be 3-conductor, 16-18 gauge, shielded. System power requirement is 90 to 240 VAC, 47 to 63 Hz. The controller shall be tested to CSA, UL, CE, FCC and IP54 standards. The FCS controller should be installed in a dry area such as a locked electrical room. Model FCS-B (BACnet output) or FCS-M (Modbus output) (up to 128 remote digital transmitters). Systems with more than thirty-two digital electrochemical sensor/transmitters will require a remote power supply Model RPS-24VDC to support the extra power requirement. One remote power is required for every thirty-two remote digital electrochemical sensor/transmitters. If wiring runs are extremely long, repeaters Model LNK-XT may be required to maintain a strong signal back to the controller.

Provide remote mount digital transmitters for underground parking areas model LPT-P-TCO for Carbon Monoxide from gas engine exhaust, with an electrochemical sensor for CO with a detection range of 0 - 200 ppm. The sensor / transmitter shall be housed in a rugged, wall mount, water/dust tight ABS/polycarbonate junction box with a secured, hinged door with a built-in gasket. The remote mount transmitter shall operate on power supplied by the control panel, and shall provide a digital output signal to the control panel. Install the CO sensor at approximately 4’ to 6’ from the floor (breathing zone).

Provide remote mount digital transmitter for loading dock model LPT-P-NO2B for Nitrogen Dioxide from diesel engine exhaust, with an electrochemical sensor for NO2 with a detection range of 0 - 10 ppm. The sensor / transmitter shall be housed in a rugged, wall mount, water/dust tight ABS/polycarbonate junction box with a secured, hinged door with a built-in gasket. The remote mount transmitter shall operate on power supplied by the control panel, and shall provide a digital output signal to the control panel. Install the NO2 sensor at approximately 4’ to 6’ from the floor (breathing zone).

In all cases use liquid tight conduit hubs when entering any water tight enclosure types to maintain water tight status in any areas subject to potential wash down. Failure to do so voids any damage from water intrusion.

System operation shall be as follows: Upon detection of 25 ppm CO or 0.7 ppm NO2 the system shall illuminate the Low alarm LED, the Low alarm relays (exhaust fans) will be activated immediately. The system shall keep the fans running for a minimum of 10 minutes to avoid cycling. Upon detection of 50 ppm CO or 0.9 ppm NO2 the system shall illuminate the Mid alarm LED and the Mid alarm relays will be activated, (only if any relays are assigned to mid alarm). The system shall keep the Mid relays active for a minimum of 10 minutes. Upon detection of 100 ppm CO or 1.0 ppm NO2 the system shall illuminate the High alarm LED, the High alarm relays and audible alarm will be activated. The system shall keep the High relays active for a minimum of 10 minutes. Audible alarm can be silenced from the front panel, silence button is imbedded in the Lexan label surrounding the display. Any remote alarm devices shall be activated at this alarm level as well.

The contractor shall provide all wiring (network and analog), conduit and interconnection required for a successful installation. System shall be tested and commissioned after installation by a trained, authorized service representative of the manufacturer, with a detailed service report provided after the site visit.

Approved manufacturer:

Critical Environment Technologies Canada Inc.