Refrigerant & Hydrogen Leak Detection System for Mechanical & UPS Rooms

Provide a wall mount, programmable 4-ch controller with back-lit LCD digital display, LED alarm indication, top mounted strobe light, 80 dB audible alarm with silence / acknowledge button integrated into the Lexan label and manual emergency mushroom shut off switch all housed in a rugged, water/dust tight IP54 rated polycarbonate/ABS enclosure with secured, hinged door. The controller shall have real time display of gas concentration, and alarm status. Controller shall be capable of supporting up to four remote sensor/transmitters. Controller shall provide three dry contact relays rated 5 A @ 240VAC SPDT each for control of other devices. If information is required at a DDC/BMS the QCC comes standard with Modbus output and optional BACnet output communications protocol. Two optional analog output signals are also available if desired. Controller wiring to remote sensor/transmitter shall be 3-conductor, 16-18 gauge, and stranded, shielded in conduit. System power requirement is 90 to 240 VAC, 47 to 63 Hz or low voltage 16-30VDC or 12-28 VAC. The controller shall be tested to CSA/UL/CE, FCC and IP54 standards. Controller shall be installed outside entrance door to mechanical room at 4’ to 6’ from the floor in an area visible to anyone entering in the room.

Provide one remote mount transmitter model ART-B-R410A with an infrared sensor calibrated for R410A refrigerant with measurement range of 0-3500 ppm. The sensor shall be housed in a rugged, wall mount, ABS/polycarbonate junction box. The remote mount sensor/transmitter shall operate on power supplied by the QCC control panel, and shall provide an analog output signal (4-20 mA) to the control panel. Install the R410A sensor 12” to 24” from the floor (refrigerants are heavier than air) in an area where refrigerant leaks are most likely to occur.

Provide one remote mount transmitter model LPT-A-CCH2-100 with catalytic sensor for Hydrogen (H2) with measurement range of 0-100% LEL. The sensor shall be housed in a rugged, wall mount, ABS/polycarbonate, water/dust tight junction box with hinged, secured door. The remote mount sensor/transmitter shall operate on power supplied by the QCC control panel, and shall provide an analog output signal to the control panel. Install the H2 sensor on or near the ceiling (Hydrogen is lighter than air).

Provide two model RSH-24VDC remote audible/visual (strobe/horn) alarms. One to be installed in the mechanical room and one to be installed in the UPS room in locations visible to anyone working in either room.

System operation shall be as follows: Upon detection of 250 ppm R410A or 10% LEL H2, the system shall illuminate the Low alarm LED and top mounted strobe light on the QCC, activate one or both of the RSH-24VDC remote alarms depending on which sensor(s) have indicated a leak above the low alarm threshold and the Low alarm relay controlling the exhaust fan starter. The system shall shut off the exhaust fan(s) in the mechanical room until the level of R410A drops below the alarm threshold. The system shall activate the exhaust fan in the UPS room in the event of a Hydrogen leak until the level of H2 drops below the Low alarm threshold.

Upon detection of 250 ppm R410A or 10% LEL H2, the system shall illuminate the High alarm LED and top mounted strobe light on the QCC, activate one or both of the RSH-24VDC remote alarms depending on which sensor(s) have indicated a leak above the high alarm threshold and the High alarm relay. The system shall shut off the exhaust fan(s) in the mechanical room until the level of R410A drops below the alarm threshold. The system shall activate the exhaust fan in the UPS room in the event of a Hydrogen leak until the level of H2 drops below the High alarm threshold.

The contractor shall provide all wiring (analog), conduit and interconnection required for a successful installation. Wiring must be 16-18 gauge, stranded, shielded and preferably in conduit. System shall be tested and commissioned after installation by a trained, authorized service representative of the manufacturer, with a detailed service report provided after the site visit.

Approved manufacturer:

Critical Environment Technologies Canada Inc.